## MEMUK RO
Membracon UK Modular RO systems Input Parameters |  | Required Permeate Flow (m3/hr) | Permeate Quality Conductivity (µS/cm) | Conductivity (µS/cm) | Feed Pressure (BAR) | Container Required | Is UV Required | Feed TSS (ppm) | Feed TDS (ppm) | Chlorine (ppm) | Turbidity (NTU) | SDI | pH | Iron mg/L | Hardness mg/L as CaCO₃ | Temp °C |  | Photo of System Selected - work in progress
|  | 9 | 12 | 11 | 4 | YES | NO | 1 | 45 | 0.01 | 1 | 3 | 6 | 0.01 | 100 | 15
#VALUE!
Recovery (%) | 75
Component mark up | 30%
Calculation
Feed Flow (m3/hr) | 11.25
Reject Flow (m3/hr) | 2.25
Permeate Flow (m3/hr) | 9
Membrane Area (m2) 8080 | 37
Number of Membranes | 9
Total Membrane Area (m2) | 333
Pressure Vessels | 3
Estimated µS/cm 1st Stage | 1.078
Pump Power (kW) | 7.5
Component | Base Cost (£) |  | Marked up £ |  |  |  |  | Reverse Osmosis System |  |  |  | 9 |  | M3/hr
Boost Pump | 0 | 54310 | 0 | 70603 |  |  |  | Item |  |  |  | Formula |  | %
Carbon (Chlorine Removal) | 0 |  | 0 |  |  |  |  | Base Manufacturing Cost |  |  |  | 70603 |  |  |  |  | Alarms will appear here
Iron Removal | 0 |  | 0 |  |  |  |  | Workshop |  |  |  | 3530.15 |  | 5%
pH Adjustment - Dosing | 1400 |  | 1820 |  |  |  |  | Contingency |  |  |  | 3530.15 |  | 5%
Turbidity (NTU) | 0 |  | 0 |  |  |  |  | Social Impact |  |  |  | 1412.06 |  | 2%
TSS Treatment | 0 |  | 0 |  |  |  |  | Subtotal |  |  |  | 79075.36 |  |  |  |  | WARNING - Temperature is low check this could effect flow - Perhaps increase size of system
TDS Treatment | 0 |  | 0 |  |  |  |  | Discount |  |  |  | 0 |  | 0%
SDI Treatment | 0 |  | 0 |  |  |  |  | Estimated GM ((sell - cost) ÷ sell)) |  |  |  | 31.32%
RO system with Pretreatment 5 um Filter | 15954 |  | 20740.2
Universal unit for flushing with permeate | 700 |  | 910 |  |  |  |  | Final Sales Price (£) |  |  |  | 79075.36
RO membranes | 4140 |  | 5382
Hardness - Anti Scale Dosing | 1400 |  | 1820 |  |  |  |  | Estimated GP (sell - cost) |  |  |  | 24765.36
CIP | 4716 |  | 6130.8
UV | 0 |  | 0 |  |  |  |  | Confidential
Container | 5500 |  | 7150
Pipework | 9000 |  | 11700
Labour | 10000 |  | 13000
Shipping | 1500 |  | 1950
Second Stage RO | 0 |  | 0
Buffer Tank
Polish DI
Additional Pipework | 0 |  | 0
Additional Labour | 0 |  | 0
Note on B5: 75% Recovery is industry Standard
Note on B6: We can set Material Mark up here as drop down
Note on B9: Feed Flow - this is calculated based on Reject and Permeate flows
Note on B10: Reject flow - this is calculated based on Recovery and Permeate flows
Note on B11: Permeate Flow - Desired sizing of Rig in m3/hr
Note on B12: Area of 8080 Membrane
Note on B22: if needed based on Feed Pressure vs range
Note on B23: Calculated based on entered levels and cross referring to range and solution and cost
Note on B24: Calculated based on entered levels and cross referring to range and solution and cost
Note on B25: Calculated based on entered levels and cross referring to range and solution and cost
Note on B26: Calculated based on entered levels and cross referring to range and solution and cost
Note on B27: Calculated based on entered levels and cross referring to range and solution and cost
Note on B28: Calculated based on entered levels and cross referring to range and solution and cost

## Alarms
WARNING - Temperature is low check this could effect flow - Perhaps increase size of system
WARNING - Margin too LOW
WARNING - Conductivity of below 10 μS/cm requires second stage RO system
WARNING - SDI HIGH - Pre-treatment required; RO at risk of rapid fouling
WARNING - TDS HIGH - May require high-rejection membranes and/or pre-treatment
WARNING - TDS HIGH - Ensure proper recovery and antiscalant dosing
WARNING - TSS HIGH - Full pre-treatment required (sand/multi-media + cartridge)
WARNING - Tubidity HIGH - Must install pre-treatment (sand filter + cartridge filter)
WARNING - Pressure is too low needs Boost pump
WARNING - Iron Levels HIGH - Dedicated iron removal system
WARNING - pH Too High Risk of irreversible membrane damage
WARNING - Chlorine HIGH - Carbon + Sodium Metabisulfite (SMBS) recommended
WARNING - Iron Levels HIGH - Mandatory iron removal
WARNING - Hard Water - Antiscalant + lower recovery
WARNING -Very hard water- Softener or hardness removal

## Pricing
|  |  |  | Ecosoft | Greenline | Industrial W | Container Pricing |  | System Size | Pipework Materials etc | Power | Modules | Membranes | Labour | Shippig | Size | CIP
RO | MEMR0025 | M3/hr | 0.25 | 1700 |  |  | 10 | 3000 | 0.25 | 3000 |  | 1 | 1 | 2000 | 1000 | 0.25 | 3500
| MEMR005 |  | 0.5 | 2200 |  |  | 10 | 3000 | 0.5 | 4000 |  | 1 | 2 | 3000 | 1000 | 0.5 | 3500
| MEMR01 |  | 1 | 3500 |  |  | 10 | 3000 | 1 | 5000 |  | 1 | 4 | 4000 | 1000 | 1 | 3500
|  |  | 1.5 |  |  |  | 10 | 3000 | 1.5 | 6000 |  |  |  | 4000 | 1000 | 1.5 | 3500
| MEMR02 |  | 2 | 4500 |  |  | 12 | 3500 | 2 | 6000 | 3 | 2 | 2 | 5000 | 1000 | 2 | 3500
|  |  | 3 |  |  |  | 12 | 3500 | 3 | 7000 |  |  |  | 5000 | 1000 | 3 | 3500
| MEMR04 |  | 4 | 5500 |  |  | 20 | 5500 | 4 | 7000 | 4 | 2 | 4 | 6000 | 1500 | 4 | 3500
| MEMR06 |  | 6 | 12100 |  |  | 20 | 5500 | 6 | 8000 | 7.5 | 3 | 6 | 8000 | 1500 | 6 | 3500
| MEMR09 |  | 9 | 15954 |  |  | 20 | 5500 | 9 | 9000 | 7.5 | 3 | 9 | 10000 | 1500 | 9 | 4716
| MEMR012 |  | 12 | 23250 |  |  | 30 | 8000 | 12 | 10000 | 11 | 4 | 12 | 12000 | 2500 | 12 | 4716
| MEMR016 |  | 16 | 27500 |  |  | 40 | 10500 | 16 | 11000 | 11 | 4 | 16 | 15000 | 2750 | 16 | 4716
Universal flushing with permeate MO6/MO9 | MEMPF69 |  | 1 | 700
Membranes |  | 8040 | 1 | 460
|  | 4040 | 1 | 150
Vessels |  |  | 1 | 600
Hardness adjustment | 0-99 | Dosing | 0.25 | 0
| 0-99 |  | 0.5 | 0
| 0-99 |  | 1 | 0
| 0-99 |  | 1.5 | 0
| 0-99 |  | 2 | 0
| 0-99 |  | 3 | 0
| 0-99 |  | 4 | 0
| 0-99 |  | 6 | 0
| 0-99 |  | 9 | 0
| 0-99 |  | 12 | 0
| 0-99 |  | 16 | 0
| 100-299 |  | 0.25 | 1400
| 100-299 |  | 0.5 | 1400
| 100-299 |  | 1 | 1400
| 100-299 |  | 1.5 | 1400
| 100-299 |  | 2 | 1400
| 100-299 |  | 3 | 1400
| 100-299 |  | 4 | 1400
| 100-299 |  | 6 | 1400
| 100-299 |  | 9 | 1400
| 100-299 |  | 12 | 1400
| 100-299 |  | 16 | 1400
| 300-600 | Softner | 0.25 | 500
| 300-600 |  | 0.5 | 700
| 300-600 |  | 1 | 1000
| 300-600 |  | 1.5 | 1000
| 300-600 |  | 2 | 1500
| 300-600 |  | 3 | 1500
| 300-600 |  | 4 | 2000
| 300-600 |  | 6 | 2500
| 300-600 |  | 9 | 3000
| 300-600 |  | 12 | 3500
| 300-600 |  | 16 | 4500
pH | 5 | Short-term operation possible, may need antiscalant adjustment |  | 1400
| 6 | Monitor scaling; adjust antiscalant dosing |  | 1400
| 8.5 | Standard polyamide membranes |  | 0
| 9 | Risk of irreversible membrane damage |  | 2500
| 12 | Risk of irreversible membrane damage |  | 3000
UV | MEMUV0025 |  | 0.25 | 400
| MEMUV005 |  | 0.5 | 400
| MEMUV010 |  | 1 | 500
| MEMUV015 |  | 1.5 | 700
| MEMUV020 |  | 2 | 825
| MEMUV030 |  | 3 | 1500
| MEMUV040 |  | 4 | 2000
| MEMUV060 |  | 6 | 2500
| MEMUV090 |  | 9 | 3000
| MEMUV120 |  | 12 | 3737
| MEMUV160 |  | 16 | 4300
Iron Level (mg/L) | 0-0.02 | Cartridge filter only | 0.25 | 0
| 0-0.02 |  | 0.5 | 0
| 0-0.02 |  | 1 | 0
| 0-0.02 |  | 1.5 | 0
| 0-0.02 |  | 2 | 0
| 0-0.02 |  | 3 | 0
| 0-0.02 |  | 4 | 0
| 0-0.02 |  | 6 | 0
| 0-0.02 |  | 9 | 0
| 0-0.02 |  | 12 | 0
| 0-0.02 |  | 16 | 0
| 0.021-0.05 | Fine filtration + monitoring | 0.25 | 1500
| 0.021-0.05 |  | 0.5 | 1500
| 0.021-0.05 |  | 1 | 1500
| 0.021-0.05 |  | 1.5 | 1500
| 0.021-0.05 |  | 2 | 1500
| 0.021-0.05 |  | 3 | 1500
| 0.021-0.05 |  | 4 | 1500
| 0.021-0.05 |  | 6 | 1500
| 0.021-0.05 |  | 9 | 1500
| 0.021-0.05 |  | 12 | 1500
| 0.021-0.05 |  | 16 | 1500
| 0.051-0.1 | Iron removal recommended | 0.25 | 3500
| 0.051-0.1 |  | 0.5 | 3500
| 0.051-0.1 |  | 1 | 3500
| 0.051-0.1 |  | 1.5 | 3500
| 0.051-0.1 |  | 2 | 3500
| 0.051-0.1 |  | 3 | 3500
| 0.051-0.1 |  | 4 | 3500
| 0.051-0.1 |  | 6 | 3500
| 0.051-0.1 |  | 9 | 3500
| 0.051-0.1 |  | 12 | 3500
| 0.051-0.1 |  | 16 | 3500
| 0.1-0.3 | Mandatory iron removal | 0.25 | 6000
| 0.1-0.3 |  | 0.5 | 6000
| 0.1-0.3 |  | 1 | 6000
| 0.1-0.3 |  | 1.5 | 6000
| 0.1-0.3 |  | 2 | 6000
| 0.1-0.3 |  | 3 | 6000
| 0.1-0.3 |  | 4 | 6000
| 0.1-0.3 |  | 6 | 6000
| 0.1-0.3 |  | 9 | 6000
| 0.1-0.3 |  | 12 | 6000
| 0.1-0.3 |  | 16 | 6000
| 0.3-5 | Dedicated iron removal system | 0.25 | 10000
| 0.3-5 |  | 0.5 | 10000
| 0.3-5 |  | 1 | 10000
| 0.3-5 |  | 1.5 | 10000
| 0.3-5 |  | 2 | 10000
| 0.3-5 |  | 3 | 10000
| 0.3-5 |  | 4 | 10000
| 0.3-5 |  | 6 | 10000
| 0.3-5 |  | 9 | 10000
| 0.3-5 |  | 12 | 10000
| 0.3-5 |  | 16 | 10000
Free chlorine mg/L | 0-0.05 | RO only | 0.25 | 0
| 0-0.05 |  | 0.5 | 0
| 0-0.05 |  | 1 | 0
| 0-0.05 |  | 1.5 | 0
| 0-0.05 |  | 2 | 0
| 0-0.05 |  | 3 | 0
| 0-0.05 |  | 4 | 0
| 0-0.05 |  | 6 | 0
| 0-0.05 |  | 9 | 0
| 0-0.05 |  | 12 | 0
| 0-0.05 |  | 16 | 0
| 0.051-1 | Carbon filter mandatory | 0.25 | 500
| 0.051-1 | Carbon filter mandatory | 0.5 | 500
| 0.051-1 | Carbon filter mandatory | 1 | 750
| 0.051-1 | Carbon filter mandatory | 1.5 | 1000
| 0.051-1 | Carbon filter mandatory | 2 | 2000
| 0.051-1 | Carbon filter mandatory | 3 | 3000
| 0.051-1 | Carbon filter mandatory - 2 of 18x65 Carbon Units | 4 | 4000
| 0.051-1 | Carbon filter mandatory | 6 | 4300
| 0.051-1 | Carbon filter mandatory | 9 | 4300
| 0.051-1 | Carbon filter mandatory | 12 | 5000
| 0.051-1 | Carbon filter mandatory | 16 | 8000
| 1.0-5 | Carbon + Sodium Metabisulfite (SMBS) recommended | 0.25 | 1900
| 1.0-5 |  | 0.5 | 1900
| 1.0-5 |  | 1 | 2150
| 1.0-5 |  | 1.5 | 2400
| 1.0-5 |  | 2 | 3400
| 1.0-5 |  | 3 | 4400
| 1.0-5 |  | 4 | 5400
| 1.0-5 |  | 6 | 5700
| 1.0-5 |  | 9 | 5700
| 1.0-5 |  | 12 | 6400
| 1.0-5 |  | 16 | 9400
Feed Boost Pump | 3 |  |  | 2000
| 10 | No boost pump needed |  | 0
Turbidity (NTU) | 0-1 | RO only | 0.25 | 0
| 0-1 | RO only | 0.5 | 0
| 0-1 |  | 1 | 0
| 0-1 |  | 1.5 | 0
| 0-1 |  | 2 | 0
| 0-1 | RO only | 3 | 0
| 0-1 | RO only | 4 | 0
| 0-1 | RO only | 6 | 0
| 0-1 | RO only | 9 | 0
| 0-1 | RO only | 12 | 0
| 0-1 | RO only | 16 | 0
| 1.1-5 | Consider cartridge + multimedia pre-filter | 0.25 | 200
| 1.1-5 |  | 0.5 | 500
| 1.1-5 |  | 1 | 1000
| 1.1-5 |  | 1.5 | 1000
| 1.1-5 |  | 2 | 1000
| 1.1-5 |  | 3 | 1500
| 1.1-5 |  | 4 | 1500
| 1.1-5 |  | 6 | 1500
| 1.1-5 |  | 9 | 2000
| 1.1-5 |  | 12 | 2000
| 1.1-5 |  | 16 | 2500
| 5.1-100 | Must install pre-treatment (sand filter + cartridge filter) | 0.25 | 500
| 5.1-100 |  | 0.5 | 500
| 5.1-100 |  | 1 | 500
| 5.1-100 |  | 1.5 | 500
| 5.1-100 |  | 2 | 1000
| 5.1-100 |  | 3 | 1000
| 5.1-100 |  | 4 | 1000
| 5.1-100 |  | 6 | 1500
| 5.1-100 |  | 9 | 2000
| 5.1-100 |  | 12 | 2500
| 5.1-100 |  | 16 | 3000
TSS (mg/L) | 0-1 | Standard 5 µm cartridge filter sufficient | 0.25 | 0
| 0-1 |  | 0.5 | 0
| 0-2 |  | 1 | 0
| 0-3 |  | 1.5 | 0
| 0-4 |  | 2 | 0
| 0-5 |  | 3 | 0
| 0-1 |  | 4 | 0
| 0-1 |  | 6 | 0
| 0-1 |  | 9 | 0
| 0-1 |  | 12 | 0
| 0-1 |  | 16 | 0
| 1.1-5 | Consider cartridge + multimedia pre-filter | 0.25 | 200
| 1.1-5 |  | 0.5 | 500
| 1.1-5 |  | 1 | 1000
| 1.1-5 |  | 1.5 | 1000
| 1.1-5 |  | 2 | 1500
| 1.1-5 |  | 3 | 1500
| 1.1-5 |  | 4 | 1500
| 1.1-5 |  | 6 | 1500
| 1.1-5 |  | 9 | 2000
| 1.1-5 |  | 12 | 2500
| 1.1-5 |  | 16 | 3000
| 5.1-100 | TSS HIGH - Full pre-treatment required (sand/multi-media + cartridge) | 0.25 | 500
| 5.1-100 |  | 0.5 | 1000
| 5.1-100 |  | 1 | 1000
| 5.1-100 |  | 1.5 | 1000
| 5.1-100 |  | 2 | 1000
| 5.1-100 |  | 3 | 1000
| 5.1-100 |  | 4 | 1000
| 5.1-100 |  | 6 | 1500
| 5.1-100 |  | 9 | 2000
| 5.1-100 |  | 12 | 2500
| 5.1-100 |  | 16 | 3000
TDS (mg/L) | 0-500 | Standard low-pressure RO membrane | 0.25 | 0
| 0-500 |  | 0.5 | 0
| 0-500 |  | 1 | 0
| 0-500 |  | 1.5 | 0
| 0-500 |  | 2 | 0
| 0-500 |  | 3 | 0
| 0-500 |  | 4 | 0
| 0-500 |  | 6 | 0
| 0-500 |  | 9 | 0
| 0-500 |  | 12 | 0
| 0-500 |  | 16 | 0
| 501-999 | Feed TDS HIGH - Ensure proper recovery and antiscalant dosing | 0.25 | 700
| 501-999 |  | 0.5 | 700
| 501-999 |  | 1 | 700
| 501-999 |  | 1.5 | 700
| 501-999 |  | 2 | 700
| 501-999 |  | 3 | 700
| 501-999 |  | 4 | 700
| 501-999 |  | 6 | 700
| 501-999 |  | 9 | 700
| 501-999 |  | 12 | 700
| 501-999 |  | 16 | 700
| 1000- 10000 | Feed TDS HIGH - May require high-rejection membranes and/or pre-treatment | 0.25 | 500
| 1000- 10000 |  | 0.5 | 500
| 1000- 10000 |  | 1 | 500
| 1000- 10000 |  | 1.5 | 500
| 1000- 10000 |  | 2 | 1000
| 1000- 10000 |  | 3 | 1000
| 1000- 10000 |  | 4 | 1000
| 1000- 10000 |  | 6 | 1500
| 1000- 10000 |  | 9 | 2000
| 1000- 10000 |  | 12 | 2500
| 1000- 10000 |  | 16 | 3000
SDI (15 min) | 0-5 | Standard cartridge filters sufficient | 0.25 | 0
| 0-5 |  | 0.5 | 0
| 0-5 |  | 1 | 0
| 0-5 |  | 1.5 | 0
| 0-5 |  | 2 | 0
| 0-5 |  | 3 | 0
| 0-5 |  | 4 | 0
| 0-5 |  | 6 | 0
| 0-5 |  | 9 | 0
| 0-5 |  | 12 | 0
| 0-5 |  | 16 | 0
| 5.1-6 | Monitor pre-filters; consider multi-media filtration | 0.25 | 200
| 5.1-6 |  | 0.5 | 250
| 5.1-6 |  | 1 | 250
| 5.1-6 |  | 1.5 | 250
| 5.1-6 |  | 2 | 500
| 5.1-6 |  | 3 | 500
| 5.1-6 |  | 4 | 1000
| 5.1-6 |  | 6 | 1500
| 5.1-6 |  | 9 | 2000
| 5.1-6 |  | 12 | 2500
| 5.1-6 |  | 16 | 3000
| 6.1-10 | SDI HIGH - Pre-treatment required; RO at risk of rapid fouling | 0.25 | 500
| 6.1-10 |  | 0.5 | 550
| 6.1-10 |  | 1 | 550
| 6.1-10 |  | 1.5 | 550
| 6.1-10 |  | 2 | 800
| 6.1-10 |  | 3 | 800
| 6.1-10 |  | 4 | 1300
| 6.1-10 |  | 6 | 1800
| 6.1-10 |  | 9 | 2300
| 6.1-10 |  | 12 | 2800
| 6.1-10 |  | 16 | 3300
Note on B121: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required
Note on B156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required
Note on B189: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required
Note on B222: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required
Note on B255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required

## ROI
Ongoing annual costs | Electricity | 10000
| Membrane replacement & chemicals | 5000
| Maintenance labor | 5000
One-time costs | RO system purchase | 79075.36
| Installation & commissioning | 12000
| Training & internal labor | 5000
| Total ongoimg costs | 20000
| Total one-time cost | 96075.36
| Total Year-1 Cost | 116075.36
Before RO | Municipal water purchase | 70000
After RO | Makeup water cost | 10000
Annual Water Savings |  | 60000
Wastewater Discharge Savings | Reduced wastewater volume and TDS Annual discharge fees | 20000
Production Efficiency / Revenue Impact | Improved water quality reduces downtime & rejects Additional annual production revenue | 15000
| Gross margin | 20%
Incremental Profit |  | 3000
Total Annual Benefits |  | 83000
ROI Y1 |  | -28.49%
| Annual net benefit | 63000
| Payback Period | 1.525
Ongoing Annual ROI (Year 2 onward) | Annual costs (O&M only) | 20000
| Annual net benefit | 63000
| Payback Period | 1.525
Ongoing Annual ROI (Year 3 onward) | Total Costs (3 years) | 156075.36
| Total Benefits (3 years) | 249000
| 3-Year ROI Calculation | 59.54%
Payback Confirmation | Annual net benefit | 63000
| Payback Period Years | 1.525
not checked or validated

## Feed Spec Notes
Paramiter | Range | Solution
Iron Level (mg/L) | < 0.02 | Cartridge filter only
| 0.02 – 0.05 | Fine filtration + monitoring
| 0.05 – 0.1 | Iron removal recommended
| > 0.1 | Mandatory iron removal
| > 0.3 | Dedicated iron removal system
Hardness | 100 | RO only | Feed is Soft
| 100-200 | Antiscalant dosing | Feed is Moderately hard
| 200-300 | Antiscalant + lower recovery | Feed is Hard - Antiscalant + lower recovery
| 300 | Softener or hardness removal | Feed is very hard - Softener or hardness removal
Free chlorine mg/L | 0 | RO only
| < 0.05 | Carbon filter or SMBS mandatory | Activated Carbon Filter (Most Common) SMBS (Sodium Metabisulphite) Dosing
| 0.1 – 1.0 | Carbon + SMBS recommended
Turbidity (NTU) | 1 | Standard 5 µm cartridge filter
| 1 – 5 | Pre-treatment recommended; consider multi-media filtration
| 5 | Must install pre-treatment (sand filter + cartridge filter)
TSS (mg/L) | ≤ 1 | Standard 5 µm cartridge filter sufficient
| 1 – 5 | Consider cartridge + multimedia pre-filter
| > 5 | Full pre-treatment required (sand/multi-media + cartridge)
TDS (mg/L) | ≤ 500 | Standard low-pressure RO membrane
| 500 – 1000 | Ensure proper recovery and antiscalant dosing
| > 1000 | May require high-rejection membranes and/or pre-treatment
Temperature (°C) | 5–45 °C | Standard low-pressure RO membranes
| < 5 °C | Reduced permeate flux; risk of freezing in cold climates
| > 45 °C | Membrane damage possible; need high-temperature membrane
SDI (15 min) | ≤ 5 | Standard cartridge filters sufficient
| 5 – 6 | Monitor pre-filters; consider multi-media filtration
| > 6 | Pre-treatment required; RO at risk of rapid fouling
pH (at RO inlet) | 6 – 8.5 | Standard polyamide membranes
| 5 – 6 | Short-term operation possible, may need antiscalant adjustment
| 8.5 – 9 | Monitor scaling; adjust antiscalant dosing
| < 5 | Risk of irreversible membrane damage
| > 9 | Risk of irreversible membrane damage
Feed Pressure | 3 | too low needs Boost pump
| 10 | No boost pump needed
Note on A11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UK mains chlorine: 0.2–0.8 ppm (typical) RO allowable chlorine: < 0.05 ppm Target: 0.00 ppm Dechlorination: Always required

## Flux temp correction
Typical RO Flux vs Temperature
Temperature Correction Factor (TCF) is a way to normalize RO membrane performance to a reference temperature (almost always 25 °C). It accounts for how water viscosity changes with temperature, which directly affects permeate flow.
Feed Temp (°C) | Temp Correction Factor (TCF) | Flux (LMH) | % of 25 °C Flux
5 | 0.45 | 9 | 45%
10 | 0.58 | 12 | 58%
15 | 0.75 | 15 | 75%
20 | 0.88 | 18 | 88%
25 | 1 | 20 | 100%
30 | 1.15 | 23 | 115%
35 | 1.3 | 26 | 130%

## Photo
0.25 | #VALUE!
0.5 | #VALUE!
1 | #VALUE!
1.5 | #VALUE!
2 | #VALUE!
3 | #VALUE!
4 | #VALUE!
6 | #VALUE!
9 | #VALUE!
12 | #VALUE!
16 | #VALUE!

## Drop Down
Feed Temp (°C) | Margin | UV / Container | Size
5 | 10% | YES | 0.25
10 | 20% | NO | 0.5
15 | 30% |  | 1
20 | 35% |  | 1.5
25 | 40% |  | 2
30 | 50% |  | 3
35 |  |  | 4
6
9
12
16